Lead-Water Testing

Results from 2020 between 5-15 ppb  
(Lavatory sinks are exempt/signage posted)

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Building | Total 5-15 ppb  in 2020 | Bathroom sinks 5-15 | Outlet Removed | **Additional**  **Samples** | **Sampled**  **10/2023** | **Results 5 or above**  **10/2023** |
| AES | 1 |  | 1 |  | **0** |  |
| FMS | 6 | 4 | 2 |  | **2** | **0** |
| GES | 14 | 1 | 2 |  | **11** | **7** |
| GHS | 31 | 25 | 1 | **2** | **7** | **5** |
| LES | 11 | 1 | 1 |  | **9** | **4** |
| PBE | 3 |  |  |  | **3** | **2** |
| WES | 6 |  | 1 |  | **5** | **2** |
| District Total | 72 | 31 | 8 | 2 | **37** | **21** |

AES:

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Space # | Room#, Location | Result 2020 | Remediation | Result 2023 | Comments |
| AES 64 | Room 403 Fountain | 5.3 | Removed | N/A | Fountain removed |

FMS:

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Space # | Room#/Location | Result 2020 | Remediation | Result 2023 | Comments |
| FMS 06 | **Art 502 Sink Left** | 6.3 | Filter/aerator | **<1.0** | **Sampled 10-12-23** |
| FMS 127 | Girl’s bathroom 986A Sink Left | 9.2 | New plumbing |  | Bathroom |
| FMS 133 | Men’s bathroom 634 Sink | 5.7 | Replaced shut-off, faucet |  | Bathroom |
| FMS 168 | **Room 434 fountain** | 5.6 | Replaced shut-off | **2.5** | **Sampled 10-12-23** |
| FMS 242 | Bathroom 986-B Sink Left | 8.0 | New plumbing |  | Bathroom |
| FMS 306 | Nurse’s Office Bathroom sink | 5.7 | Replaced faucet, shut-off |  | Bathroom |

GES:

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Space# | Room#/Location | Result 2020 | Remediation | Result 2023 | Comments |
| GES 14 | **Room 106 sink** | 6.6 | Replaced Filter-aerator | **7.0** | **Sampled 10-5-23** |
| GES 34 | Boy’s Locker Room 148 Sink | 10.1 | Removed |  | Removed |
| GES 40 | **Room 504 Sink** | 5.0 | Replaced Filter/Shutoff | **15.8** | **Sampled 10-5-23** |
| GES 43 | **Room 505 Sink** | 8.4 | Replaced Filter-aerator | 1.4 | **Sampled 10-5-23** |
| GES 45 | **Room 507 Sink** | 7.0 | Replaced Filter-aerator | **6.2** | **Sampled 10-5-23** |
| GES 46 | **Room 508 Sink** | 7.0 | Replaced Filter-aerator | 4.8 | **Sampled 10-5-23** |
| GES 57 | **Room 604 Sink** | 6.1 | Replaced Shut-off | **12.4** | **Sampled 10-5-23** |
| GES 59 | **Room 603 Sink** | 6.1 | Replaced Shut-off | **8.2** | **Sampled 10-5-23** |
| GES 60 | **Room 606 Sink** | 14.8 | Replaced Filter-aerator | 4.2 | **Sampled 10-5-23** |
| GES 86 | **Art Room 404 Sink Right** | 7.1 | Replaced shut-off, faucet | **18.9** | **Sampled 10-5-23** |
| GES 97 | **Room 506 Sink** | 5.6 | Replaced shut-off | **5.7** | **Sampled 10-5-23** |
| GES 106 | Room 206 Fountain | 8.7 | Removed/all new plumbing |  | Removed |
| GES 107 | **Room 206 Sink** | 6.9 | Removed/ all new plumbing | 2.6 | **Sampled 10-5-23** |
| GES 113 | Girl’s bathroom 611A | 10.8 |  |  | Bathroom |

GHS:

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Space# | Room#/Location | Result 2020 | Remediation | Result 2023 | Comments |
| GHS-East: |  |  |  |  |  |
| E-05 | Girl’s PE office bathroom sink | 7.9 | Replaced faucet, shut-offs |  | Bathroom |
| E-07 | Bathroom 138, Sink, Middle | 7.2 | No middle sink |  | Bathroom |
| E-08 | Bathroom 138 Sink Right | 6.0 | Replaced faucet, shut-offs |  | Bathroom |
| E-09 | Bathroom 136 Sink Right | 6.0 | Replaced faucet, shut-offs |  | Bathroom |
| E-10 | Bathroom 136 Sink Middle | 8.4 | Replaced faucet, shut-offs |  | Bathroom |
| E-13 | Boy’s East PE Office Bathroom Sink | 5.7 | Replaced faucet, shut-off |  | Bathroom |
| E-18 | Bathroom 211 Sink Right | 5.3 | Filter-mixer |  | Bathroom |
| E-44 | Room 403 Sink, Replaced | 14.8 | New Science Room, new sinks |  | Removed in Capital Project after 2020 |
| E-96 | Bathroom 413 Sink Middle | 5.6 | Replaced faucet, shut-offs |  | Bathroom |
| E-97 | Bathroom 413 Sink Left | 7.8 | Replaced faucet, shut-offs |  | Bathroom |
| E-169 | **Technology Shop 3, Sink Left** | 14.5 | **Replaced faucet** | **20.3** | **Sampled 10-12-23, near Door C5** |
| E-170 | **Technology Shop 3, Sink Right** | 8.7 | **Replaced faucet** | **13.1** | **Sampled 10-12-23 near Door C5** |
| E-170A\* | **Technology Sink Left** |  | **None, not identified as 5-15 see note below\*** | **30.4** | **Sampled 10-12-23 near door C6** |
| E-170B\* | **Technology Sink Right** |  | **None, not identified as 5-15 see note below\*** | **8.6** | **Sampled 10-12-23 near door C6** |
| \*While sampling, we added the above two outlets on as a precaution because they had Do Not Drink signage and teacher thought they were the ones that needed testing. Created new sample numbers. | | | | | |
| E-180 | Men’s bathroom 311 Sink | 5.4 | Replaced faucet, shut-off |  | Bathroom |
| E-41-B | Girl’s bathroom by Café A sink Left. | 7.3 | Filter |  | Bathroom |
| GHS West: |  |  |  |  |  |
| W-30 | Bathroom by Room 22 Sink | 11.3 | Replaced faucet, shut-off |  | Bathroom |
| W-33 | **Kitchen dishwashing sink, middle** | 11.8 | Replaced faucet | **1.6** | **Sampled 10-12-23** |
| W-38 | **New Cafeteria A, Sink**  **(2023 sampled sink behind service counter).** | 5.2 | **None not found during remediation** | **15.7** | **Sampled 10-12-23** |
| W-41 | Girl’s bathroom by  Café A, Sink Left | 10.4 | Filter |  | Bathroom |
| W-42 | Girl’s bathroom by  Café A Middle | 6.7 | Filter |  | Bathroom |
| W-43 | Girl’s bathroom by  Café A Sink Right | 5.4 | Filter |  | Bathroom |
| W-46 | Boy’s bathroom by Café A Sink Right | 8.6 | Filter, mixer |  | Bathroom |
| W-47 | **Small Cafeteria Sink** | 5.8 | **Filter, aerator** | **4.6** | **Sampled 10-12-23, but was difficult to get water out of.** |
| W-59 | West Boy’s Locker Bathroom Sink Left | 7.4 | Filter, mixer |  | Bathroom |
| W-77 | Faculty Men’s bathroom Sink | 5.3 | Replaced faucet, lines |  | Bathroom |
| W-81 | Assistant Principal’s bathroom sink | 5.2 | Replaced faucet, lines |  | Bathroom |
| W-106 | Boy’s bathroom 609A Right Sink, Left | 5.0 | Filter, lines |  | Bathroom |
| W-123 | 2nd girl’s bathroom 717A Right Sink, Left | 12.4 | Filter |  | Bathroom |
| W-124 | 2nd Girl’s bathroom 717A Right Sink, Middle | 8.2 | Filter |  | Bathroom |
| W-125 | 2nd Girl’s bathroom 717A Right Sink, Right | 9.0 | Filter |  | Bathroom |
| W-126 | 2nd Girl’s bathroom Right Sink, Left | 6.0 | Filter |  | Bathroom |
| W-128 | 2nd Girl’s bathroom 717A Left Sink, Right | 9.1 | Filter |  | Bathroom |

LES:

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Space | Room#/Location | Result 2020 | Remediation | Result 2023 | Comment |
| LES 10 | Room 154 Sink | 5.2 | Replaced filter/aerator | **<1.0** | **Sampled 10-5-23** |
| LES 15 | **Room 151 Sink** | 5.4 | Replaced faucet-shutoffs | **6.1** | **Sampled 10-5-23** |
| LES 17 | Room 110 Fountain | 6.7 | Removed |  | Removed |
| LES 19 | **Room 109 Sink** | 6.4 | Replaced aerator | 1.6 | **Sampled 10-5-23** |
| LES 29 | **Room 114 Sink** | 5.7 | Replaced shut-off, faucet | 5.0 | **Sampled 10-5-23** |
| LES 35 | **Music 129 Sink** | 5.5 | Replaced faucet and lines | **25** | **Sampled 10-5-23** |
| LES 40 | Kitchen Bathroom Sink | 7.4 | Replaced faucet and shut-offs |  | Bathroom |
| LES 42 | Kitchen Handwash Sink | 12.6 | Replaced shut-offs | 1.1 | **Sampled 10-5-23** |
| LES 59 | **Room 406 Sink** | 5.5 | Replaced faucet | **9.3** | **Sampled 10-5-23** |
| LES 72 | **Room 505 Sink** | 5.6 | Replaced aerator | 4.8 | **Sampled 10-5-23** |
| LES 74 | **Room 110 Sink** | 8.6 | Replaced shut-offs and faucet | **8.6** | **Sampled 10-5-23** |

PBE:

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Space | Room#/Location | Result 2020 | Remediation | Result 2023 | Comment |
| PBE 30 | **Special Ed. 201 Sink** | 9.2 | Replaced faucet, shut-offs | **5.5** | **Sampled 10-5-23** |
| PBE 51 | **Music 605 Sink** | 7.9 | Filter | <1.0 | **Sampled 10-5-23** |
| PBE 87 | **Kitchen back corner Sink** | 9.9 | Filter | **86.9** | **Sampled 10-5-23**  **Sink not being used.** |

WES:

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Space | Room#/Location | Result 2020 | Remediation | Result 2023 | Comments |
| WES 29 | Room 125 Fountain | 5.1 |  |  | Removed |
| WES 30 | **Room 125 Sink** | 8.8 | All new plumbing | **10.8** | **Sampled 10-5-23** |
| WES 51 | **Room 119 Sink** | 7.7 | Filter | <1.0 | **Sampled 10-5-23** |
| WES 55 | **Room 117 Sink** | 5.0 | Filter | 4.5 | **Sampled 10-5-23** |
| WES 88 | **Room 144 Sink** | 5.1 | Filter | <1.0 | **Sampled 10-5-23** |
| WES 97A | **Room 212, fountain** | 5.2 | Replaced shut-offs, faucet, drain | **7.7** | **Sampled 10-5-23 Pressure only a trickle** |